## Cover Sheet
Needed Fire Flow (NFF) Calculation Worksheet
For Residential Buildings, see Tab 1 - Residential Fire Flow
For Non-Residential Buildings with a fully sprinklered system, see Tab 2 - Non-Residential Sprinkler
Print and Sign Tab 3 - Sign off sheet
Preparer: Please fill in only the yellow shaded cells on worksheets
Municipal Fire Official or assigned Delegate: Please fill in only the blue shaded cells as appropriate on Sign Off Sheet
The ability of a distribution system to provide safe, adequate and reliable service to its customers is analyzed based on forecasted customer demands and the Needed Fire Flow (NFF). Hydraulic computer modeling of the distribution system is utilized as the primary tool in the analysis. The model will determine system adequacy/deficiency and evaluate the effectiveness of proposed improvements under requested fire demand conditions. Published manuals from the ISO are used as a guide in determining the NFF. The calculations and tables contained within are obtained from the ISO's Guide For Determination of Needed Fire Flow, Edition 06-2014.
*This worksheet is only a guide and in no way does New Jersey American Water take responsibility for the calculated Needed Fire Flow indicated within. In some cases the requested Needed Fire Flow for a site may be more or less based on other factors not accounted for in this worksheet. ISO’s municipal fire protection testing may identify sites with needed fire flows greater than 3,500 gpm for a duration of three hours. In many pressure zones, particularly in residential areas, the identified maximum is less than 3,500 gpm. Where individual structures are assigned ISO Needed Flows above 3,500 gpm, fire protection needs in excess of 3,500 gpm at these sites will be satisfied through the development of individual customer-owned fire suppression systems.
References: Guide for Determination of Needed Fire Flow. Rep. 06-2014 ed. N.p.: Insurance Services Office, 2014. Print. Fire Suppression Rating Schedule. Rep. N.p.: Insurance Services Office, 2012. Print.

## 1 - Residential Fire Flow
1. Residential
Needed Fire Flow (NFF) (Refer to Table and Notes below) |  |  | *Example* | GPM @ 20 psi
750
For 1- and 2-family dwellings not exceeding 2 stories with an Effective Area* of 4800 Square Feet or less, use the following Needed Fire Flows:
Distance Between Buildings |  | Needed Fire Flow
More than 30 feet |  | 500 gpm
21-30 feet |  | 750 gpm
11-20 feet |  | 1,000 gpm
0-10 feet |  | 1,500 gpm
Residential with Automatic Fire Sprinkler System
For a 1- or 2-family dwelling protected with an automatic fire sprinkler system installed in accordance with the general criteria of NFPA 13D, Installation of Sprinkler Systems for One-and Two-Family Dwellings and Manufactured Homes, the Needed Fire Flow is either the demand at the base of the automatic sprinkler riser or 500 gpm, whichever is greater.
The NFF for residential occupancies (such as apartment buildings, lodgings and rooming houses, board and care facilities, hotels, motels and dormitories) protected by an automatic fire sprinkler system installed in accordance with the general criteria of NFPA 13R, Standard for the Installation of Sprinkler Systems in Residential Occupancies up to and including Four Stories in Height, is either the demand at the base of the automatic sprinkler riser or 1000 gpm, whichever is greater.
Residential with Effective Area* of greater than 4800 square feet
For a 1- or 2-family dwelling with an Effective Area* greater than 4,800 square feet, refer to ISO's Guide for Determination of Needed Fire Flow, Edition 06-2014.
* To calculate Effective Area refer to ISO's Guide for Determination of Needed Fire Flow, Edition 06-2014.
References: Guide for Determination of Needed Fire Flow. Rep. 06-2014 ed. N.p.: Insurance Services Office, 2014. Print. Fire Suppression Rating Schedule. Rep. N.p.: Insurance Services Office, 2012. Print.

## 2 - Non-Residential Sprinklered
2. Non-Residential, Fully Sprinklered
Fill in the Demand at the Base of the Automatic Sprinkler Riser and the NFPA 13 Hose Stream Demand
For projects with multiple buildings, fill out for the highest demand building. | GPM @ 20 psi
Demand at the Base of the Automatic Sprinkler Riser
NFPA 13 Hose Stream Demand
Needed Fire Flow (NFF) * | 0
* Minimum NFF is 500 GPM
If a fire pump is required, please provide the following information
Pump Flow Rate | GPM
Total Dynamic Head | feet
Notes
The Needed Fire Flow (NFF) for commercial occupancies protected by an automatic fire sprinkler system installed in accordance with the general criteria of NFPA 13, Standard for Installation of Sprinkler Systems, is the demand at the base of the automatic sprinkler riser and inside/outside hose stream demand. For Non-Residential, not fully sprinklered buildings refer to ISO's Guide for Determination of Needed Fire Flow, Edition 06-2014.
References: Guide for Determination of Needed Fire Flow. Rep. 06-2014 ed. N.p.: Insurance Services Office, 2014. Print. Fire Suppression Rating Schedule. Rep. N.p.: Insurance Services Office, 2012. Print.

## 3 - Sign Off Sheet
3 - Sign Off Sheet
Residential Fire Flow
Needed Fire Flow (per ISO) |  |  | 0 | GPM @ 20 psi
Total Needed Fire Flow (if higher flow amount requested by township official) |  |  |  | GPM @ 20 psi
Non-Residential, Fully Sprinklered
Needed Fire Flow (per ISO) |  |  | 0 | GPM @ 20 psi
Total Needed Fire Flow (if higher flow amount requested by township official) |  |  |  | GPM @ 20 psi
Note: Please Provide Both Signatures
Project Name:
Project Address:
Prepared By:
Signature:
Title:
Date:
Phone #
Signing this sheet is only an acknowledgement of the NFF.
It does not imply a review and approval of the NFF calculations.
Municipal Fire Official or Delegate
(Print name):
Municipality
Signature:
Title:
Date:
Phone #

## Sheet1 (hidden)
Yes | 1.5
No | 1.0
| 0.8 | (250*ROUND(18*I20*(I21^(0.5))/250,0))
| 0.6 | 18*I20*(I21^(0.5))